## Power analysis
Compass of the Four Winds Power Calculations
BY: | Eduardo Ortega
DATE: | 2018-04-26
Part Nunber of LED Used in Strip | SK6812
Voltage Vcc for LED | 5 | Volts
Drive Current for LED's (Amps/LED) | 0.06 | Amps/LED
LEDs / Meter | 30
Top Insignia | 45 | LED used
Bottom Answer | 50
Lining of Throne/Totem | 4
Number of Throne/Totem | 4
Compass LED | 0.5
Number of sides / face | 1
Realistic LED Brightness Operating Factor | 0.3 | NOTE: EACH COLOR WILL ONLY UTILIZE 1/3 OF THE AMPAGE
Realistic COLOR Operating Factor | 1
| Meters Used | Amps Used WHITE | Max Power WHITE (Watts, Worst Case) | Power at REALISTIC BRIGHTNESS | Power at REALISTIC COLOR & BRIGHTNESS | Amps Used at REALISTIC COLOR & BRIGHTNESS | Watts Used at REALISTIC & BRIGHTNESS
Totem (ALL 4) | 396 | 712.8 | 3564 | 1069.2 | 1069.2 | 213.84 | 1069.2
Compass | 0.5 | 0.9 | 4.5 | 1.35 | 1.35 | 0.27 | 1.35
TOTALS | 396.5 | 713.7 | 3568.5 | 1070.55 | 1070.55 | 214.11 | 1070.55
AC TO DC POWER SUPPIES SELECTED
AC TO DC CONVERSION EFFICIENCY | 90% | (Usual Aproximate factor)
Factor for Oversizing Generator | 50%
Generator Performance Factor | 100%
Power to Select Generator Needed | Oversized factor Generator Needed @ MAX WHITE | Oversized Factor Generator Needed @ Realistic Load
TOTALS | 5709.6 | 1712.88
% of full load | 0.5705 | 0.17115
Fuel Consumption | 0.76915 | 0.52474
Generator Selected | KUBOTA GL1100
Generator Single Phase 120V Output Amps | 83.4 | Amps | 10008 | Watts
| Full LOAD | 3/4 LOAD | 1/2 LOAD | 1/4 LOAD
Gallons of Fuel / Hour | 1.05 | 0.86 | 0.71 | 0.59
NOTE: BASED OFF OF LINEAR APPROXIMATIONS FROM THE KUBOTA GL1100 Datasheet
In order to prevent wet Stacking one should run the Generator beween 30% and 60% of load for long periods
Load | Fuel Consumption (Gallon/hour)
1 | 1.05
0.75 | 0.86
0.5 | 0.71
0.25 | 0.59
| Gallons/Hour | Hours/day | Number of Days | Number of gallons needed
Cases: Fuel Needed (general) | Rate of Fuel Consumed | Conversation | Duration | Fuel Used
100% for 9 days | 1.05 | 24 | 9 | 226.8
70% for 9 days | 0.8469 | 24 | 9 | 182.9304
50% for 9 days | 0.7115 | 24 | 9 | 153.684
30% for 9 days | 0.5761 | 24 | 9 | 124.4376
NOTE: Realistically, we will run it during the night for 12 hours every day (9 days)
| Gallons/Hour | Hours/day | Number of Days | Number of gallons needed
Cases: Fuel Needed for LED | Rate of Fuel Consumed | Conversation | Duration | Fuel Used
MAX Load | 0.76915 | 12 | 9 | 83.068
Realistic Load | 0.52474 | 12 | 9 | 56.6724

## Circuit analysis
LED Strip SK6812
Length of 1 unit (m) | 1
LED/m | 30
A/LED | 0.06 | NOTE: Assume white (worst case) for initial analysis
A/m | 1.8
Totem Analysis | Lining used (both sides) | Top insginia | Throne answer
LED strip used | 4 | 45 | 50
Amps Needed | 7.2 | 81 | 90
Amps Needed with Performance factor | 2.4 | 27 | 30
Total | 36 | 81 | 90
Total with performance factor | 12 | 27 | 30
Compass Analysis | Compass Spin
LED strip used | 0.5
Meters per Side | 0.9
Amps Needed | 0.45
Amps Needed with Performance Factor | 0.15
Total | 2.25
Total with performance factor | 0.75
Performance Factor | 0.33333